## Slide 1: PID Control
An Overview

## Slide 2
PID is a form of automatic feedback control based on error
Error is the difference between the variable under control y(t) and a reference u(t)
P, I, D are mathematical operations applied to the error to generate the process actuating signal
What is PID control?

## Slide 3
3
Where does PID come from?
James Watt’s flyball governor in 1788: P-only control
PID first used for governor control in 1890’s
Nicolas Minorsky researched automatic steering systems for US Navy ships in 1922
Observed steering actions of experienced helmsmen
Helmsmen controlled ship based not only on current error, but also past error and current rate of change
Formalised observations as mathematical equations
Successfully trialled aboard USS New Mexico, but ultimately not adopted due to “resistance by personnel”

## Slide 4
4
The mathematical operations of multiplication, integration and differentiation have proved easy to implement with the technology of the day
    Mechanical
    Pneumatic
    Electronic analog
    Electronic digital
Very low computational overhead for large scale digital processor systems
Simple to configure and tune
Has proven to be robust and stable
Handles unmeasured disturbances well
Does not require a model
Why is PID used so extensively?

## Slide 5
5
What is a typical PID implementation on a plant?

## Slide 6
6
You can only control what you can measure
Instrument calibration
– neccessary!

## Slide 7
7
Or, thank goodness for automation engineers!
Direct vs Reverse control direction
  Most control systems don’t take negative gains, so…
  Should the controller output increase with increasing PV, or decrease?
    Increase → Direct, e.g. Level-to-flow out
    Decrease → Reverse, e.g. Flow control
PID configurable parameters: Decisions to make upfront

## Slide 8
8
PID configurable parameters: Decisions to make upfront (2)

## Slide 9
9
PID configurable parameters: Decisions to make upfront (3)

## Slide 10
10
PID configurable parameters: Tuning

## Slide 11
11
PID configurable parameters: Tuning (2)

## Slide 12
12
PID configurable parameters: Tuning (3)
TF
  PV filter time constant
  Unit in Minutes / seconds
  Contribution to change in output: None
  Role is to reduce PV signal “noise” so PID does not act on it

## Slide 13
13
Tuning: Different approaches

## Slide 14
14
Incremental tuning assumes a few things:
    A valid starting point (NB!)
    User experience
    A good imagination
…and has some characteristics:
    Not repeatable or systematic (art)
    Evaluation dependent on process conditions
Control response design assumes a few things:
    You may step change the process
    Process responses are more or less consistent
    Some mathematical ability, and a good imagination
…and has some characteristics:
    Recipe-based and quantifiable (science)
    Evaluation dependent on measuring objectives
Incremental tuning vs Control response design

## Slide 15
15
Open vs Closed loop responses

## Slide 16
16
How do you characterize a response?

## Slide 17
17
0.632
Dead time (θ)
Time constant (τ (=Tau))
0.98
Time to Steady State (TTSS)
≈ 4×τ
How do you characterize a response?

## Slide 18
18
The real world

## Slide 19
19
Approximation 1
Dead time (θ)≈ 5 min
Time constant (τ)
≈ 5.5 min

## Slide 20
20
Approximation 2
Dead time (θ)≈ 5 min
0.632
Time constant (τ)
≈ 4.5 min

## Slide 21
21
The main objective of response design is to get a desired control speed of response with minimum actuator travel
What is the objective of response design?
0.632
Closed loop time constant (λ)

## Slide 22
22
λ sets the desired speed of response of the control loop
λ is always judged relative to the open loop time constant τ:
  λ << τ – Tuned “fast / overshoot”
  λ ≈ τ – Tuned “normal”
  λ >> τ – Tuned “slow” / “buffering action”
What is important about the closed loop time constant λ?

## Slide 23
23
0.632
2.7
3.7
5
2.7
3.7
5
The effect of closed loop time constant: Setpoint change

## Slide 24
24
TTSS ≈ 4×2.7=10.8
TTSS ≈ 4×3.7=14.8
TTSS ≈ 4×5=20.0
2.7
3.7
5
2.7
3.7
5
The effect of closed loop time constant: PV disturbance

## Slide 25
25
There are many tuning rules
E.g. Ziegler-Nichols, Cohen-Coon, Internal Model Control
Usually the underlying basis: λ and damping, is pre-selected and hidden
IMC, Internal Model Control, is an approach to solve, for a given model, the tuning parameters which gives a critically damped closed loop response with time constant = λ
Also known as “Lambda” tuning
Opens up the design process so that speed of response can be specified by the user
Control response design = Tuning rules?

## Slide 26
26
Proportional Action: How to calculate K

## Slide 27
27
Proportional Action: How to calculate K (2)

## Slide 28
28
Integral Action: How to calculate Ti

## Slide 29
29
Derivative Action: How to calculate Td and TF
Theoretically, Td only helps with S-shaped (2nd order / higher) open loop responses, therefore primarily temperature and composition, not flow and pressure
Expect ~20% improvement from a base of good PI, not a “miracle cure” for bad PI
Practically, this means 0.33 to 0.5 θ in most cases (θ ≤ τ)
TF is very important to filter a noisy PV otherwise noise is transferred to actuator movement
Rule of thumb:

## Slide 30
30
θ
0.632
SS
τ
A calculation example

## Slide 31
31
A calculation example

## Slide 32
32
A calculation example (2)

## Slide 33
33
A calculation example (3)

## Slide 34
34
A calculation example (4)

## Slide 35
35
A calculation example (5)

## Slide 36
36
A calculation example (6)

## Slide 37
37

## Slide 38
38
Increase cooler recuperation efficiency
    Increase SAT/TAT
    Cooler control
Decrease preheater losses
    Decrease preheater exit O2
    Gas flow control
Decrease preheater losses
    Decrease preheater exit temperature
    precalciner temperature control
3 Actions to decrease kJ/kg cli Kiln operation actions that you can implement now

## Slide 39
39
Step 1: Stabilize SAT/TAT
Step 2: Increase SAT/TAT
Step 3: Reduce fuel rate
→ Lower Heat consumption
Cooler Control

## Slide 40
40
SAT/TAT are a function of clinker temperature - cannot control
SAT/TAT are a function of air residence time through clinker
  clinker bed height
  air speed in recuperation zone
For stable short-term SAT/TAT (0-60 minutes):
  Stabilize clinker bed height
  Stabilize air speed in recuperation zone
Longer term stability of SAT/TAT is separate issue
Cooler Control Step 1: Stabilize SAT/TAT – Clinker bed height

## Slide 41
41
UGP usually has excellent short-term relationship to SAT/TAT
Increase UGP → increase SAT/TAT and vice-versa
Defining UGP
  Select earliest UGP measurement in cooler which is reliable
  Reason: improved control loop dynamics
  Usually, but not always, this means fixed inlet UGP
UGP is controlled at its setpoint (mbar) by moving grate speed (spm) through the use of an automatic control loop (PID)
Cooler Control Step 1: Stabilize SAT / TAT – UnderGrate Pressure Control

## Slide 42
42
Cooler Control Step 1: Stabilize SAT/TAT – UnderGrate Pressure Control

## Slide 43
43
Cooler Control Step 1: Stabilize SAT/TAT – Early UGP measurement
Secret to good UGP control: “early” UGP measurement

## Slide 44
44
Fundamental requirement for UGP control is constant air flow in the compartment where UGP is measured
Linear relationship between UGP and fan air flow:
Cooler Control Step 1: Stabilize SAT/TAT – Stable fan flow or SP change!
Options:
  Keep air flow under UGP constant (typical if fixed inlet used), or
  Adjust UGP setpoint in fan table according to flow relationship

## Slide 45
45
Example: Fan table, if UGP is in compartment 2
Example: Tests show that +2,000 Am3/h = +2 mbar UGP
Cooler Control Step 1: Stabilize SAT/TAT – Stable fan flow or SP change!
Feed t/h | UGP SP mbar | Fan 1 Am3/h | Fan 2 Am3/h | Fan 3 Am3/h | Fan 4 Am3/h | Fan 5 Am3/h | Fan 6 Am3/h
200 | 70 | 35,000 | 20,000 | 20,000 | 22,000 | ... | ...
220 | 72 | 35,000 | 22,000 | 22,000 | 24,000 | ... | ...
240 | 74 | 35,000 | 24,000 | 24,000 | etc... | ... | ...
260 | 76 | 35,000 | 26,000 | 26,000 | ... | ... | ...
280 | 78 | 35,000 | 28,000 | 28,000 | ... | ... | ...

## Slide 46
46
If new to PID tuning, apply following steps
Guide values (starting point)
  Kp = 1.0
  Ti = 480s
  Td = 0s
Decrease UGP setpoint of existing PCS PID by 3 mbar
Observe UGP response in PCS. Good result is:
  UGP reaches new setpoint within 10 minutes
  Overshoot of max 1-2 mbar
Repeat test in other direction
If taking too long to reach setpoint, decrease Ti and vice-versa
Stability benchmark: stdev of UGP at constant SP: <2 mbar*
Stdev UGP 2 mbar = ~ stdev SAT 20°C*, stdev TAT 25°C
*= minutely spot data from TIS, typical thermocouple
Cooler Control Step 1: Stabilize SAT/TAT – Grate Speed PID Tuning

## Slide 47
47
Now that short-term UGP has been stabilized, we can operate more safely with higher clinker bed (= higher SAT/TAT)
Simply increase the UGP setpoint +3 mbar
Observe results over 24 hours
Did SAT/TAT clearly increase sustainably over 24 hrs.?
  If yes (most common starting case), repeat test, setpoint +3 mbar
Did SAT/TAT do nothing?
  If yes, return UGP to setpoint
  Maybe try decreasing UGP setpoint -3 mbar, observe over 24 hrs.
----------------------------------------------------------------------------------
Did SAT/TAT decrease?
  If yes, decrease UGP setpoint -3 mbar, observe over 24 hrs.
Cooler Control Step 2: Increase SAT/TAT – Simple Steps

## Slide 48
48
If TAT has increased, and precalciner temperature is controlled by PID, then the fuel rate to precalciner will decrease automatically
If SAT has increased:
  Operator needs to reduce fuel manually (no BZT PID)
  Should occur “automatically” because free lime will decrease
  May not occur if operator continues to use his “normal” fuel rate to main burner
Cooler Control Step 3: Decrease Fuel to main burner and precalciner

## Slide 49
49

## Slide 50
50
Step 1: Gas flow stabilization
Gas Flow Control
Step 2: Oxygen stabilization
Step 3: Reduce oxygen content
Step 4: Reduce fuel feedrate
→ Lower Heat consumption

## Slide 51
51
Oxygen vs. gasflow
  What is the difference?
  Influences on O2 content:
    NCV
    Fuel feeding
    Kiln feeding
  What should we be controlling?
Step 1: Gas flow Stabilization
Concept:
  Stable material to gas relationship
  Stable velocities in PH tower & kiln

## Slide 52
52
Two cases
Step 1: Gas flow Stabilization
No disturbance before ID fan
Disturbance(s) before ID fan
Coal mill

## Slide 53
53
Calculation
Direct measurement
  Promecon (ca 20 kUSD)
Flow=
kWFanmotor·η
ΔpFan
Step 1: Measurement of gas flow

## Slide 54
54
Fan flow:
Maintain flow constant (short term)
  Maintain ID fan speed
  Maintain dp across fan
    Stable outlet pressure → Filter fan loop
    Stabilize water control loop → minimize influence → tune PID
    Coal mill start stop procedure → minimize influence with SOP
    Raw mill start/ stop procedure → minimize influence with SOP
Maintain pressure at PH outlet constant with ID fan speed
  Implemented in some plants (usually in 2 fan systems)
  Frequent adjustment of pressure SP required
Step 1: Manual “control” of gas flow
Calculation
Flow=
kWFanmotor·η
ΔpFan

## Slide 55
55
Step 1: minimize influences of coal mill stops

## Slide 56
56
Measurement: Kiln inlet probe
Control:
  Tertiary air damper: Strategy to minimize wear:
    Normally almost completely open
    Adjustment of dp with additional resistances in TAD
Step 1: Control of Gasflow at kiln inlet

## Slide 57
57
Kiln inlet
Recommended suppliers:
  FLS Airloq, ENOTEC, SICK, ABB
  Placement critical: Protect probe from falling coating
Difficult measurement but with right probe and right location continuous measurement possible
Preheater exit
As replacement of PC exit
Less maintenance in this location
Insitu (e.g.ENOTEC) or extractive measurement
Sinter metal probe
Double probe to avoid cleaning spikes
Step 2: measurement of oxygen

## Slide 58
58
Stable gas flow
Stable energy inputs
  Cooler control to stabilize recuperation
  precalciner control to stabilize energy input
    AFR (energy) compensation
    Proper PID tuning of loop
Control of Kiln inlet oxygen
  Working tertiary air damper and kiln inlet probe
  Maintaining kiln inlet oxygen level should not require excessive oxygen level at preheater exit
Step 2: Stabilize O2

## Slide 59
59
Step 3: Reduce O2 content
  Minimum required to avoid excessive CO formation
  Any reserve is additional heat consumption
  Check
    Preheater velocities if running at low production rates
    Orifice velocity to ensure proper meal pick up
  Typically 0.5 – 1% at PC exit ( lowest stage cyclone are sufficient)
Step 4: Reduce fuel feedrate
→ Lower Heat consumption
Step 3: Reduce Oxygen content

## Slide 60
60
With lower gasflow and better heat recuperation in cooler fuel feedrate at precalciner/preheater can be lowered.
No heat consumption reduction if this is not been done
Step 4: Reduce fuel feedrate

## Slide 61
61

## Slide 62
62
Step 1: Stabilize PCT
Step 2: Decrease PCT → Decrease preheater losses
Step 3: Reduce fuel rate
→ Lower Heat consumption
Precalciner Temperature (PCT) Control

## Slide 63
63
PCT usually means bottom cyclone exit temperature
PCT is related to calcination degree by the “calcination curve”
Note: Calcination reaction itself is fast at <95% (1-3s)
Precalciner Temperature Control Step 1: Stabilize PCT

## Slide 64
64
Key #1 to good PCT control:
  Fast temperature measurement (or at least, not slow)
  Main issue is thermowell thickness, sometimes thermocouple
Precalciner Temperature Control Step 1: Stabilize PCT – Fast Thermocouple Measurement
Measurement is only at the junction

## Slide 65
65
Precalciner Temperature Control Step 1: Stabilize PCT – Fast Thermocouple Measurement

## Slide 66
66
Key #2 to good PCT control: Well tuned PID controller!
Guide values (starting point)
  Kp = 0.2
  Ti = 200s
  Td = 0s
Increase PCT setpoint +10°C
Observe PCT response in PCS. Good result is:
  PCT reaches new setpoint after ~15 minutes
  Little or no overshoot
Repeat test in other direction
Precalciner Temperature Control Step 1: Stabilize PCT – PCT PID Tuning

## Slide 67
67
Stability benchmark depends on PCT setpoint and AFR%
All values are standard deviations of control error (PV-SP)
Precalciner Temperature Control Step 1: Stabilize PCT – PCT PID Tuning
 | 0% AFR | 50%AFR | 100%AFR
870°C SP | 2°C | 5°C | 8°C
920°C SP | 3°C | 7.5°C | 12°C

## Slide 68
68
Stable PCT → Reduce PCT setpoint → Lower PH exit temp. → Lower heat losses → Lower STEC
The precalciner was invented in order to separate the calcination and the sintering processes
  More efficient heat transfer of gas with powder
  Not necessary to combust the fuel for calcination in the sintering zone
  Not necessary to transport the combustion gases and CO2 from raw meal calcination through the kiln
Allows higher kiln capacities for the same rotary kiln diameter
In principle therefore, we want the material leaving the precalciner to have a very high calcination degree → high temperature
BUT, high temperature = higher preheater exit temperature
Precalciner Temperature Control Step 2: Reduce precalciner Exit Temperature (PCT)

## Slide 69
69
This temperature scale varies between plants and so this graph cannot directly be applied to your precalciner
Precalciner Temperature Control Step 2: Reduce precalciner Exit Temperature (PCT)
Δ Calcination
Δ T°C
Δ Calcination
Δ T°C
Difficult to control calcination using temperature
Easier to control calcination using temperature

## Slide 70
70
This temperature scale varies between plants and so this graph cannot directly be applied to your precalciner
Precalciner Temperature Control Step 2: Reduce precalciner Exit Temperature (PCT)
Δ Calcination
Δ T°C
Δ Calcination
Δ T°C
No problems
Easier to overheat, cause build-ups, waste fuel

## Slide 71
71
Because we are using a PID, the fuel rate will decrease automatically!
Precalciner Temperature Control Step 3: Reduce Fuel Rate

## Slide 72
72

## Slide 73
73
Get out of your office to the CCR!
    A setpoint used for 20 years does not mean that it is the optimum!
Check and optimize
    Increase cooler recuperation (UGP)
    Lower precalciner temperature (PCT)
    Minimize and stabilize gas flow (PH O2)
PID loop well tuned utilized by the operators. If not in use: Tuning required!
Minimize kiln stops with maintenance
Summary